# CoolMaster Edge Product Terminal Command-Line

This guide describes every command available in the ng_asciif command-line interface, the text-based console used to configure and operate CoolAutomation HVAC controllers. Commands are typed directly at the prompt by name — there is no need to prefix them with a menu or module name.

Some commands have one or more alternate names (aliases) that produce identical or very similarly formatted output; where relevant, the differences between aliases are called out in that command’s entry.

## Table of Contents

- General / System

  - exit

  - date

  - reboot

  - boot

  - commit

- Network Configuration

  - ifconfig

- GPIO

  - gpio

  - gpio norm

  - gpio func

- HVAC Line & Unit Control

  - ls

  - stati

  - info

  - line

  - on

  - off

  - filt

  - mode

  - fan

  - dry

  - heat

  - cool

  - auto

  - fspeed

  - SP

  - RT

  - louver

  - lock

  - link

- Device Settings

  - set

  - set aserver

  - set baud

  - set defaults

- Status Query

  - query

- Lutron Integration

  - lutron

  - lutron discover

  - lutron pair

  - lutron bind

  - lutron unpair

- Simulation

  - simul

- Status Reports

  - istat

  - ostat

  - systat

- Device Properties

  - props

- BACnet

  - bacnet

  - bacnet ip

  - bacnet name

  - bacnet id

  - bacnet list

- Cloud Connection

  - coolhost clear

  - coolhost

- Power

  - power

- Virtual Addressing

  - va

  - va delall

  - va auto

  - va +

  - va -

## General / System

### exit

Description: Ends the current CLI session.

Parameters: None

Example:

exit

### date

Description: Prints the controller’s current system date and time, followed by the standard “OK” status line.

Parameters: None

Example:

date
Sun Jul  5 17:32:10 UTC 2026
OK

### reboot

Description: Immediately reboots the entire controller. Produces no console output before the connection drops.

Parameters: None

Example:

reboot

### boot

Description: Applies all pending configuration changes made by other commands (such as ifconfig, bacnet ip, or gpio func) and restarts the affected services. The boot_mode parameter is accepted for compatibility but has no effect.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| boot_mode | text | No | 2 | Boot mode (accepted but currently has no effect) |

Example:

boot

### commit

Description: Same effect as boot: applies all pending configuration changes and restarts the affected services.

Parameters: None

Example:

commit

## Network Configuration

### ifconfig

Description: With no arguments, prints the LAN interface’s MAC address, link state, IP/DHCP status, netmask, gateway, DNS servers, autoip state, and receive error count. With a sub-verb, it changes one aspect of the LAN network configuration (static/DHCP IP, admin up/down, autoip, gateway, netmask, or DNS).

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| subcom | switch | No | (none — shows status) | Sub-verb selecting what to configure |

Sub-verbs:

| Sub-verb | Value | Description |
| --- | --- | --- |
| IP | IP address | Set a static IP address, or DHCP to switch the interface to DHCP |
| enable | (none) | Bring the LAN interface up |
| disable | (none) | Bring the LAN interface down |
| Autoip | 0 or 1 | Enable (1) or disable (0) link-local (autoip) addressing |
| Gateway | IP address | Set the default gateway |
| Netmask | IP address | Set the subnet mask |
| DNS1 | IP address | Set the primary DNS server |
| DNS2 | IP address | Set the secondary DNS server |

Example:

ifconfig
MAC    : AA:BB:CC:DD:EE:FF
Link   : Up
IP     : 192.168.1.50 (Static)
Netmask: 255.255.255.0
Gateway: 192.168.1.1
DNS1   : 8.8.8.8
DNS2   : 0.0.0.0
Autoip : No(0)
Rx err : 0

ifconfig IP 192.168.1.50
OK

ifconfig IP DHCP
OK

ifconfig enable
OK

ifconfig Gateway 192.168.1.1
OK

## GPIO

### gpio

Description: Prints the status of every configured GPIO line, showing its assigned function, current value, and normal state (Normally Open / Normally Closed).

Parameters: None

Example:

gpio
  A: OOS     (1), N.O.
  B: Unused  (0)

### gpio norm

Description: Sets whether a GPIO line’s normal (inactive) state is Normally Open or Normally Closed.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| line | text | Yes | — | GPIO line to configure: A or B |
| norm | text | Yes | — | Normal state: O/o = Normally Open, C/c = Normally Closed |

Example:

gpio norm A o
OK, Boot Required!

### gpio func

Description: Sets the function assigned to a GPIO line. The ALL function additionally takes an action verb (OFF/ON/INH) controlling how all indoor units behave when the line transitions between its Normal and Active states.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| line | text | Yes | — | GPIO line to configure: 1 or 2 |
| func | text | Yes | — | Function: Unused, ALL, OOS, FLRS, BI, BO, AI |
| action | text (only when func is ALL) | Yes (if func=ALL) | — | OFF, ON, or INH — behavior applied to all indoor units on the state transition |

Example:

gpio func 1 OOS
OK, Boot Required!

gpio func 2 ALL INH
OK, Boot Required!

## HVAC Line & Unit Control

This is the largest command group, covering HVAC communication lines and indoor-unit control.

### ls

Aliases: ls2, stat, stat2, stat3, stat4 — same command, different output formatting: - ls2: setpoint and room temperature shown to 1 decimal place, full address, plus filter and therm-on flags. - stat: address printed without the line prefix, setpoint rounded to an integer, room temperature shown to 2 decimal places, no trailing flags. - stat2: same as stat but with a trailing filter flag appended. - stat3: setpoint and room temperature both rounded to integers, short address, trailing filter flag only. - stat4: setpoint and room temperature both rounded to integers, short address, trailing filter flag and therm-on flag.

Description: Queries the live status of one or more indoor units matching an address pattern, printing one line per unit showing on/off state, setpoint/room temperature, fan speed, mode, and failure code. If no units match, prints a “No UID” error.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| dev_addr_ptrn | text | No | * | Indoor unit address — * (all), L1 (whole line), or L1.100 (one unit). Wildcards within an address (e.g. L1.*) are not supported. |

Example:

ls L1.100
L1.100 ON  30C 26C High Fan  OK   # 0

### stati

Description: Fetches a short identifying string for indoor unit(s) and prints each device address followed by that string — for normal units an ID:<hex> value, for BACnet-origin units a BACNET: <name> (...) description.

Parameters: None

Example:

stati
L1.100 ID:D4664610

### info

Description: Reports the on/off state and voltage of the 16V DC output line on line L2.

Parameters: None

Example:

info
L2 DC+ 16V

### line

Description: Configures or reports on HVAC communication lines. With no subcommand, prints a summary of all HVAC lines (type, line-specific extra info such as Modbus address for CG5, unit/group counts, and Tx/Rx/timeout/checksum/collision/NAK/arbitration statistics). With a subcommand, updates a single setting of the given line and prints OK, Boot Required! on success, or an error code on invalid input.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| subcom | switch | No |  | Selects one of the sub-verbs below; omitting it prints the line summary |

Example:

line
L1: DK U03/G03
    Tx:120 Rx:118 TO:0 CS:0 Col:0 NAK:0 ARB:0
L2: Unused
    Tx:0 Rx:0 TO:0 CS:0 Col:0 NAK:0 ARB:0

line sub-verbs:

| Sub-verb | Parameters | Description | Example |
| --- | --- | --- | --- |
| baud | line (e.g. L1), value (baud rate, e.g. 9600..115200), optional_value (optional serial format, e.g. 8N1) | Sets the UART baud rate for a line; if optional_value is supplied it is appended with an underscore (e.g. 9600_8N1). | line baud L1 9600 8N1 → OK, Boot Required! |
| version | None | Prints the firmware/version string of the HVAC line service — not a per-line setting. | line version → 0.0.8 |
| polarity | line (e.g. L1), value (A\¦B, B\¦A, or auto) | Sets the RS-485 wiring polarity for a line; rejects any other value with “Bad Parameter”. | line polarity L1 auto → OK, Boot Required! |
| DCOUT | line (e.g. L1), value (- or +) | Switches the line’s 16V DC output on (+) or off (-). | line DCOUT L2 + → OK, Boot Required! |
| termination | line (e.g. L1), value (0 or 1) | Enables/disables the RS-485 bus termination resistor for a line. | line termination L1 1 → OK, Boot Required! |
| type | line (e.g. L1), value (e.g. DK, GMV5SI, BACNET, MODBUS, Unused) | Changes the line’s protocol/brand type. unused removes the line’s configuration entirely; BAC/BACNET also enables the corresponding BACnet MSTP interface (L1-L3 only). Value is upper-cased before storage. | line type L1 GMV5SI → OK, Boot Required! |
| simul | line (e.g. L1), value (integer count) | Sets the number of simulated HVAC devices on a line (for bench/lab testing); rejects non-numeric values. | line simul L1 5 → OK, Boot Required! |
| myid | line (e.g. L1), value (hex, up to 32 bits) | Sets the controller’s own bus address/ID on the given line; must be a valid hex value. | line myid L1 0B → OK, Boot Required! |
| master | line (e.g. L1), value (0 or 1) | Sets whether this controller acts as bus master (1) or slave (0) on the given line. | line master L1 1 → OK, Boot Required! |
| scan | line (e.g. L1), value (0 or 1) | Enables/disables the initial device scan performed at boot for the given line. | line scan L1 1 → OK, Boot Required! |
| tpl | line (e.g. L1), value (template name, e.g. GMV5SI0, MESI0) | Applies a predefined bundle of line/device settings to the line in one shot, replacing its existing configuration; unknown template names return “Out of Range”. | line tpl L1 MESI0 → OK, Boot Required! |

L1 TTM x:on

### on

Aliases: allon — behaves identically to on (its help text says “Turn on all HVAC lines”, which is already the effective behavior of on when no pattern is given, since the default pattern is *).

Description: Turns on the HVAC line/indoor units matching the address pattern. If the pattern doesn’t already look like L<n> or L<n>.<addr>, it is automatically rewritten to match across all lines.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| dev_addr_ptrn | text | No | * | Indoor unit address pattern |

Example:

on L1.100
OK

### off

Aliases: alloff — identical behavior; only its help text (“Turn off all HVAC lines”) differs.

Description: Turns off the HVAC line/indoor units matching the address pattern.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| dev_addr_ptrn | text | No | * | Indoor unit address pattern |

Example:

off L1.100
OK

### filt

Description: Resets the filter sign on indoor unit(s) matching the address pattern. A bare pattern without an L<n> prefix is rewritten to match across all lines; omitting the address (or passing *) resets every unit.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| dev_addr_ptrn | text | No | * | Indoor unit address pattern |

Example:

filt L1.102
OK

### mode

Description: Sets the HVAC operating mode (e.g. Cool/Heat/Auto/Dry/Fan) for indoor units matching the address pattern.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| dev_addr_ptrn | text | No | * | Indoor unit address pattern |
| hvac_mode | text | No | None | HVAC mode |

Example:

mode L1.100 Cool
OK

### fan

Description: Convenience command that always sets the HVAC mode to Fan for units matching the address pattern.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| dev_addr_ptrn | text | No | * | Indoor unit address pattern |

Example:

fan L1.100
OK

### dry

Description: Convenience command that always sets the HVAC mode to Dry for matching units.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| dev_addr_ptrn | text | No | * | Indoor unit address pattern |

Example:

dry L1.100
OK

### heat

Description: Convenience command that always sets the HVAC mode to Heat for matching units.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| dev_addr_ptrn | text | No | * | Indoor unit address pattern |

Example:

heat L1.100
OK

### cool

Description: Convenience command that always sets the HVAC mode to Cool for matching units.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| dev_addr_ptrn | text | No | * | Indoor unit address pattern |

Example:

cool L1.100
OK

### auto

Description: Convenience command that always sets the HVAC mode to Auto for matching units.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| dev_addr_ptrn | text | No | * | Indoor unit address pattern |

Example:

auto L1.100
OK

### fspeed

Description: Sets the HVAC fan speed for units matching the address pattern. The single-letter shorthand v/l/m/h/t/a maps to VLow/Low/Med/High/Top/Auto respectively; any other value is passed through as-is.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| dev_addr_ptrn | text | No | * | Indoor unit address pattern |
| fspeed_mode | text | No | None | HVAC fan speed (v,l,m,h,t,a shorthand, or a full name) |

Example:

fspeed L1.100 h
OK

### SP

Aliases: temp — identical parameters/behavior.

Description: Sets the HVAC setpoint temperature for matching units. If the display unit setting is F, the entered value is converted from Fahrenheit to Celsius before being applied.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| dev_addr_ptrn | text | No | * | Indoor unit address pattern |
| setpoint | text | No | None | HVAC setpoint |

Example:

SP L1.100 24
OK

### RT

Aliases: feed — identical parameters/behavior.

Description: Sends a room-temperature feedback reading for matching units. If the display unit setting is F, the entered value is converted from Fahrenheit to Celsius first, same as SP.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| dev_addr_ptrn | text | No | * | Indoor unit address pattern |
| room_temp | text | No | None | HVAC room temperature |

Example:

RT L1.100 24
OK

### louver

Aliases: swing — not behaviorally identical: louver maps shorthand letters to full position names before sending, and applies the change as a louver position. swing sends the raw lower-cased value un-mapped and applies the change as a swing setting instead.

Description: Sets the louver/swing position for matching units. Maps the shorthand letters h/v/a/3/4/6/- to Horz/Vert/Swing/30/45/60/Stop respectively (when invoked as louver).

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| dev_addr_ptrn | text | No | * | Indoor unit address pattern |
| state | text | No | None | Louver state (h,v,a,3,4,6,- shorthand, or a full name) |

Example:

louver L1.100 h
OK

### lock

Description: Shows or changes the HVAC keypad/remote lock flags for units matching the address pattern. If no lock_string is given, prints each matching device’s current flags. If a lock_string is given, it is parsed as either a bare +/- (lock/unlock everything) or a sequence of +/--prefixed flag letters — o (on/off), m (mode), t (setpoint), n (on) — and the resulting change is applied.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| dev_addr_ptrn | text | No | * | Indoor unit address pattern |
| lock_string | text | No | None | +¦-[o¦m¦t¦n]: +/- = full lock/unlock; +o/-o = on-off; +m/-m = mode; +t/-t = setpoint; +n/-n = “on” |

Example:

lock L1.100
L1.100: +o +m -t

lock L1.100 +m-t
OK

### link

Description: Manages address-to-model link entries. With both arguments empty, lists all existing links (index, address, model). With both arguments given, adds a new link mapping arg1 (device address, using Y in place of L, e.g. Y1.100) to arg2 (model name). If only arg1 is given and matches a negative-number pattern (e.g. -2), deletes the link entry at that index instead; any other combination has no effect.

NOTE: Currently applies to Toshiba

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| arg1 | text | No | None | Device address to link, L written as Y (e.g. Y1.100); or -N to delete link index N; omit with arg2 to list all links |
| arg2 | text | No | None | Model name to associate with arg1 (only used when adding a link) |

Example:

link
L000: Y1.100  >  SMMSu

link Y1.100 SMMSu
OK, Boot Required!

link -0
OK, Boot Required!

## Device Settings

### set

Description: With no arguments, prints the device’s current settings snapshot (serial number, firmware version, build date, baud rate, echo/verbose flags, aserver port/enable, temperature unit, melody). With a sub-verb and value, updates the corresponding setting immediately — no separate commit command is required.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| subcom | switch | No | None | Sub-verb selecting which setting to change; omit both subcom and value to just print current settings |

Sub-verbs:

| Sub-verb | Value | Description |
| --- | --- | --- |
| verbose | 1 or 0 | Enable/disable verbose error-string output (vs. numeric error codes) |
| deg | C or F | Set the displayed temperature unit |
| echo | 1 or 0 | Enable/disable command echo |
| melody | 1 or 0 | Select the startup melody/sound |

Example:

set
S/N          : 050048E3
version      : 0.9.2 (PCB Rev 5.7)
baud rate    : 9600
echo         : 1
verbose      : 0
deg C/F      : C
melody       : 1

set verbose 1
OK

set deg F
OK

### set aserver

Description: Configures the ASCII/BACnet application server exposed over TCP. Applies immediately, so no separate commit command is needed.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| subcom | switch | Yes | None | Sub-verb selecting which aserver parameter to set |

Sub-verbs:

| Sub-verb | Value | Description |
| --- | --- | --- |
| port | 0..65535 | TCP port the aserver listens on |
| enable | 1 or 0 | Enable[1]/disable[0] the aserver |

Example:

set aserver port 10102
OK

set aserver enable 1
OK

### set baud

Description: Sets the RS-232/console baud rate. Applies immediately.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| value | 9600¦19200¦38400¦115200 | Yes | None | New baud rate |

Example:

set baud 115200
OK

### set defaults

Description: Resets the device to factory defaults. Applies immediately — no commit is involved.

Parameters: None

Example:

set defaults
OK

## Status Query

### query

Description: Queries one or more indoor units matching a strict device-address pattern and prints a single value per matched unit, selected by the value letter. Degrees are converted to Fahrenheit first if the display unit setting is F. Prints “OK” after all matches, or “Bad Property” if the requested property can’t be read for a unit.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| dev_addr_ptrn | text | Yes | None | Device address pattern (e.g. L1.001) |
| value | text | Yes | None | Property selector: o=on/off (1/0), m=mode (0=Cool..5=Fan), f=fan speed (0=Low..7=SSHi), t=setpoint temp (integer), h=setpoint temp (float, 2dp), e=failure code (0 if OK), a=room temp (integer), s=louver/swing state |

Example:

query L1.001 t
22
OK

query L1.001 o
1
OK

## Lutron Integration

### lutron

Description: Lists the Lutron bridges currently registered on the controller. For each registered bridge, prints the bridge ID, system type, and IP address; if none are registered, prints an error instead.

Parameters: None

Example:

lutron
L1: RA2 192.168.1.50
OK

### lutron discover

Description: Searches the network for Lutron controllers, printing a status message while the search runs.

Parameters: None

Example:

lutron discover
Searching for Lutron devices on the network...

### lutron pair

Description: Pairs the device with a Lutron controller discovered on the network.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| id | text | Yes | None | Lutron bridge Id |

Example:

lutron pair id=abc123
Finding a device to pair with...

### lutron bind

Description: Pairs the device with a Lutron controller directly by IP address, bypassing network discovery.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| id | text | Yes | None | Lutron bridge Id |
| ip | IP address | Yes | None | Lutron bridge IP address |
| sys | text | No | None | Lutron bridge system type |

Example:

lutron bind id=abc123 ip=192.168.1.50 sys=RA2
Connecting 192.168.1.50...

### lutron unpair

Description: Unpairs a registered Lutron controller. Passing id=all removes every registered controller instead of a single one.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| id | text | Yes | None | Lutron bridge Id (use all to remove every registered controller) |

Example:

lutron unpair id=abc123
OK

## Simulation

### simul

Description: Runs a simulation sub-command for a given HVAC line — used for bench/lab testing without real HVAC hardware attached. When command is left empty, defaults to listing every active simulation patch and its key/value fields; other sub-commands are accepted but produce no additional listing in the current implementation.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| line | text | No | * | Line number, e.g. L1; * targets all lines |
| command | text | No | “” (treated as listing active patches) | Simulation sub-command to run |

Example:

simul L1
Patch 1
    dev  : L1.001
    prop : SP
    val  : 24
OK

## Status Reports

### istat

Description: Fetches indoor diagnostic parameters. With arg empty, queries live runtime data; with arg = ch, queries commissioning/history data instead. Any other arg value returns “Bad Parameter”. Note: the line parameter is accepted but currently has no filtering effect.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| line | text (e.g. L1) | No | None | Line number, e.g. L1 (currently has no effect) |
| arg | text | No | “” | “” = live runtime data; ch = commissioning/history data; any other value errors |

Example:

istat
X1.001 onoff: 1 SP: 21 RT: 24.500000 mode: "Auto" fspeed: "Med"

### ostat

Description: Fetches outdoor diagnostic parameters, merged together with system-level data (the same data reported by systat). Same arg/data-source behavior as istat; the line parameter is likewise accepted but has no effect.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| line | text (e.g. L1) | No | None | Line number, e.g. L1 (currently has no effect) |
| arg | text | No | “” | “” = live runtime data; ch = commissioning/history data; any other value errors |

Example:

ostat
Y1.001 status: "OK" ambient: 32.500000
   Y1.100
      Y1.100 comp_hz: 55

### systat

Description: Fetches system-level diagnostic parameters directly (the same data ostat merges in). Same arg behavior and the same non-functional line parameter as istat/ostat.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| line | text (e.g. L1) | No | None | Line number, e.g. L1 (currently has no effect) |
| arg | text | No | “” | “” = live runtime data; ch = commissioning/history data; any other value errors |

Example:

systat
Y1.001 status: "OK" ambient: 32.500000

## Device Properties

### props

Description: Prints a fixed-width table of every indoor unit’s UID, name, cool/heat setpoint limit ranges, and lock/limit flags (state/mode/setpoint/cool/heat lock indicators).

Parameters: None

Example:

props
  UID  |      Name      | Cool | Heat |   Elocks  |
-------+----------------+-------------+-----------+
L1.001 | Living Room    | 18  30|16  32| o m t     |
OK

## BACnet

### bacnet

Description: Displays BACnet integration configuration. With no argument, prints every configured BACnet interface (ip, mstp1, mstp2, mstp3, …); with an interface argument, prints only that interface’s parameters. Fails with “No BACnet License” if the BACnet feature is not licensed/available on this device.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| interface | text | No | (none) | BACnet interface to show — one of ip, mstp1, mstp2, mstp3; empty shows all |

Example:

bacnet mstp1
    apdu_retries         : 3
    apdu_timeout_ms      : 6000
    datalink             : mstp
    device_id            : 42
    device_name          : CoolMasterEdge
    dnet                 : 1
    enable               : 0
    iface                : ubev1
    model_name           : CoolMaster EDGE
    mstp_baud            : 38400
    mstp_mac             : 42
    mstp_max_info_frames : 1
    mstp_max_master      : 127
    ubus_obj_name        : bacnet.mstp1
    vendor_id            : 1164
    whois_interval_ms    : 60000
OK

### bacnet ip

Description: Configures the BACnet/IP datalink (interface, BBMD, UDP port, enable/disable). Always reports “OK, Boot Required!” since the change needs commit/boot to take effect.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| subcom | switch | Yes | — | Sub-verb selecting which BACnet/IP setting to change |

Sub-verbs:

| Sub-verb | Value | Description |
| --- | --- | --- |
| iface | text | Network interface name to bind BACnet/IP to |
| BBMD | A.B.C.D:PORT | BBMD address (or 0 to disconnect) |
| port | 0..65535 | UDP port for BACnet/IP |
| enable | 1 or 0 | Enable or disable BACnet/IP |

Example:

bacnet ip enable 1
OK, Boot Required!

bacnet ip BBMD 192.168.1.10:47808
OK, Boot Required!

### bacnet name

Description: Sets the BACnet device name for a BACnet interface. Requires a subsequent boot/commit to apply.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| name | text | Yes | — | New BACnet device name |
| interface | text | Yes | — | BACnet interface to rename — one of ip, mstp1, mstp2, mstp3 |

Example:

bacnet name CoolMasterEdge_42 ip
OK, Boot Required!

### bacnet id

Aliases: bacnet instance — identical behavior; alternate wording for the same command.

Description: Sets the BACnet device instance ID for a BACnet interface. Requires a subsequent boot/commit to apply.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| id | number (0..4194303) | Yes | — | New BACnet device instance number |
| interface | text | Yes | — | BACnet interface to update — one of ip, mstp1, mstp2, mstp3 |

Example:

bacnet id 42 ip
OK, Boot Required!

### bacnet list

Description: Fetches a list of known BACnet devices, units, or templates and pretty-prints the full raw response table (protocol envelope plus every field of each entry) — a debug-style dump, not a curated summary.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| subcom | switch | Yes | — | What to list: devices, units, or templates |

Example:

bacnet list devices
{
  "type": "bacnetDevicesGetResponse"
  "rc": 0
  "devices":   {
    "826b8686-9d54-48c5-a6e5-27979a6b1a53":     {
      "name": "X1.013"
      "bacnetId": 2281
      "online": true
      ...
    }
    ...
  }
}
OK

## Cloud Connection

### coolhost clear

Description: Wipes cloud-related connection/registration state on the device. Prints “OK” on success or “Failed” on error.

Parameters: None

Example:

coolhost clear
OK

### coolhost

Description: With no arguments, prints a formatted table of cloud connection parameters (server, ports, ping/reconnect counters, connection status, etc.). When invoked with a matching secret and a sub-verb, changes the cloud server, port, or connection security setting — any such change requires a reboot to take effect.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| secret | text | No | “” (empty) | Internal access code gating the sub-verbs below. Omit it entirely to just view cloud status; an incorrect non-empty value returns “Failed” |
| subcom | switch | No | — | Selects which cloud parameter to change once secret is valid: server, port, ssl |

Sub-verbs (under subcom):

| Sub-verb | Value param | Type | Description |
| --- | --- | --- | --- |
| server | server_val | text | New cloud server hostname; keeps the existing connection scheme/port |
| port | port_val | number (0-65535) | New cloud server TCP port |
| ssl | ssl_val | 0 or 1 | 0 selects a plain (unencrypted) connection, 1 selects a TLS-secured connection |

Example:

coolhost
remote.access  : enabled
server         : cloud.example.com
port           : 10101
ping rate      : 120
ssl            : on
portS          : 443
...
status         : enabled V3
OK

coolhost <secret> server cloud2.example.com
OK, Boot Required!

coolhost wrong-secret server cloud2.example.com
Failed

## Virtual Addressing

### va

Description: Lists the current CA-to-VA (control address to virtual address) mapping, printing entries grouped under INDOORS, PRO INDOORS, and PRO OUTDOORS sections (each shown only if present).

Parameters: None

Example:

va
INDOORS
L1.001 --> 00001
L1.002 --> 00002
OK

### va delall

Description: Clears the entire VA mapping, printing “Failed” in addition to an error message if the operation fails.

Parameters: None

Example:

va delall
OK

### va auto

Description: Recreates the VA mapping automatically. On failure only the returned error message is printed (unlike the other va subcommands, no additional “Failed” line).

Parameters: None

Example:

va auto
OK

### va +

Description: Adds a single CA-to-VA mapping entry.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| ca | text | Yes | None | Unit CA (e.g. L1.001) |
| va | number | Yes | None | Unit VA (e.g. 1) |

Example:

va + ca=L1.003 va=3
OK

### va -

Description: Deletes a VA mapping entry; the single argument may be either a CA string or a VA number — the device automatically determines which it is.

Parameters:

| Name | Type | Required | Default | Description |
| --- | --- | --- | --- | --- |
| arg | text | Yes | None | Unit CA (e.g. L1.001) or unit VA (e.g. 1) |

Example:

va - arg=L1.003
OK