## Sheet1
Encoding
Operation Mode
0 | Cool | 8 | VAM Auto
1 | Heat | 9 | VAM Bypass
2 | Auto | 10 | VAM Heat Exc
3 | Dry | 11 | VAM Normal
4 | HAUX
5 | Fan
Fan Speed
0 | Low | 5 | Very Low
1 | Medium | 7 | VAM Super High
2 | High | 8 | VAM Lo FreshUp
3 | Auto | 9 | VAM Hi FreshUp
4 | Top
Set Temperature Limits
MSB |  | LSB
15..8 |  | 7..0
High Limit x2 |  | Low Limit x2
Swing |  |  | Lock Bits
0 | Vertical |  | Bit 0 | ON/OFF
1 | 30 deg |  | Bit 1 | Mode
2 | 45 deg |  | Bit 2 | Set Temperature
3 | 60 deg |  | Bit 3
4 | Horizontal |  | Bit 7 | ALL
5 | Auto
6 | OFF
Following table is only for VA's. When all indoor units connected and organized from lowest to highest , the table below can represent indoor units (VA number = indoor unit)
VA number | 1 | Base Address = |  | 17
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
17 | Operation Mode |  | UID Ln.XYY | ON/OFF
18 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
19 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
20 | ON/OFF |  | HVAC Malfunction CD | Inhibit
21 | Filter Sign |  | Reserved | Reserved
22 | Swing
23 | Room Temperature x10 °C | RO
24 | HVAC Malfunction Code | RO
25 | Lock Bits
26 | Set Temperature Limits
27 | Reserved
28
29
30
31
32
VA number | 2 | Base Address = |  | 33
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
33 | Operation Mode |  | UID Ln.XYY | ON/OFF
34 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
35 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
36 | ON/OFF |  | HVAC Malfunction CD | Inhibit
37 | Filter Sign |  | Reserved | Reserved
38 | Swing
39 | Room Temperature x10 °C | RO
40 | HVAC Malfunction Code | RO
41 | Lock Bits
42 | Set Temperature Limits
43 | Reserved
44
45
46
47
48
VA number | 3 | Base Address = |  | 49
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
49 | Operation Mode |  | UID Ln.XYY | ON/OFF
50 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
51 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
52 | ON/OFF |  | HVAC Malfunction CD | Inhibit
53 | Filter Sign |  | Reserved | Reserved
54 | Swing
55 | Room Temperature x10 °C | RO
56 | HVAC Malfunction Code | RO
57 | Lock Bits
58 | Set Temperature Limits
59 | Reserved
60
61
62
63
64
VA number | 4 | Base Address = |  | 65
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
65 | Operation Mode |  | UID Ln.XYY | ON/OFF
66 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
67 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
68 | ON/OFF |  | HVAC Malfunction CD | Inhibit
69 | Filter Sign |  | Reserved | Reserved
70 | Swing
71 | Room Temperature x10 °C | RO
72 | HVAC Malfunction Code | RO
73 | Lock Bits
74 | Set Temperature Limits
75 | Reserved
76
77
78
79
80
VA number | 5 | Base Address = |  | 81
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
81 | Operation Mode |  | UID Ln.XYY | ON/OFF
82 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
83 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
84 | ON/OFF |  | HVAC Malfunction CD | Inhibit
85 | Filter Sign |  | Reserved | Reserved
86 | Swing
87 | Room Temperature x10 °C | RO
88 | HVAC Malfunction Code | RO
89 | Lock Bits
90 | Set Temperature Limits
91 | Reserved
92
93
94
95
96
VA number | 6 | Base Address = |  | 97
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
97 | Operation Mode |  | UID Ln.XYY | ON/OFF
98 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
99 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
100 | ON/OFF |  | HVAC Malfunction CD | Inhibit
101 | Filter Sign |  | Reserved | Reserved
102 | Swing
103 | Room Temperature x10 °C | RO
104 | HVAC Malfunction Code | RO
105 | Lock Bits
106 | Set Temperature Limits
107 | Reserved
108
109
110
111
112
VA number | 7 | Base Address = |  | 113
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
113 | Operation Mode |  | UID Ln.XYY | ON/OFF
114 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
115 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
116 | ON/OFF |  | HVAC Malfunction CD | Inhibit
117 | Filter Sign |  | Reserved | Reserved
118 | Swing
119 | Room Temperature x10 °C | RO
120 | HVAC Malfunction Code | RO
121 | Lock Bits
122 | Set Temperature Limits
123 | Reserved
124
125
126
127
128
VA number | 8 | Base Address = |  | 129
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
129 | Operation Mode |  | UID Ln.XYY | ON/OFF
130 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
131 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
132 | ON/OFF |  | HVAC Malfunction CD | Inhibit
133 | Filter Sign |  | Reserved | Reserved
134 | Swing
135 | Room Temperature x10 °C | RO
136 | HVAC Malfunction Code | RO
137 | Lock Bits
138 | Set Temperature Limits
139 | Reserved
140
141
142
143
144
VA number | 9 | Base Address = |  | 145
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
145 | Operation Mode |  | UID Ln.XYY | ON/OFF
146 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
147 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
148 | ON/OFF |  | HVAC Malfunction CD | Inhibit
149 | Filter Sign |  | Reserved | Reserved
150 | Swing
151 | Room Temperature x10 °C | RO
152 | HVAC Malfunction Code | RO
153 | Lock Bits
154 | Set Temperature Limits
155 | Reserved
156
157
158
159
160
VA number | 10 | Base Address = |  | 161
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
161 | Operation Mode |  | UID Ln.XYY | ON/OFF
162 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
163 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
164 | ON/OFF |  | HVAC Malfunction CD | Inhibit
165 | Filter Sign |  | Reserved | Reserved
166 | Swing
167 | Room Temperature x10 °C | RO
168 | HVAC Malfunction Code | RO
169 | Lock Bits
170 | Set Temperature Limits
171 | Reserved
172
173
174
175
176
VA number | 11 | Base Address = |  | 177
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
177 | Operation Mode |  | UID Ln.XYY | ON/OFF
178 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
179 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
180 | ON/OFF |  | HVAC Malfunction CD | Inhibit
181 | Filter Sign |  | Reserved | Reserved
182 | Swing
183 | Room Temperature x10 °C | RO
184 | HVAC Malfunction Code | RO
185 | Lock Bits
186 | Set Temperature Limits
187 | Reserved
188
189
190
191
192
VA number | 12 | Base Address = |  | 193
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
193 | Operation Mode |  | UID Ln.XYY | ON/OFF
194 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
195 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
196 | ON/OFF |  | HVAC Malfunction CD | Inhibit
197 | Filter Sign |  | Reserved | Reserved
198 | Swing
199 | Room Temperature x10 °C | RO
200 | HVAC Malfunction Code | RO
201 | Lock Bits
202 | Set Temperature Limits
203 | Reserved
204
205
206
207
208
VA number | 13 | Base Address = |  | 209
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
209 | Operation Mode |  | UID Ln.XYY | ON/OFF
210 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
211 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
212 | ON/OFF |  | HVAC Malfunction CD | Inhibit
213 | Filter Sign |  | Reserved | Reserved
214 | Swing
215 | Room Temperature x10 °C | RO
216 | HVAC Malfunction Code | RO
217 | Lock Bits
218 | Set Temperature Limits
219 | Reserved
220
221
222
223
224
VA number | 14 | Base Address = |  | 225
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
225 | Operation Mode |  | UID Ln.XYY | ON/OFF
226 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
227 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
228 | ON/OFF |  | HVAC Malfunction CD | Inhibit
229 | Filter Sign |  | Reserved | Reserved
230 | Swing
231 | Room Temperature x10 °C | RO
232 | HVAC Malfunction Code | RO
233 | Lock Bits
234 | Set Temperature Limits
235 | Reserved
236
237
238
239
240
VA number | 15 | Base Address = |  | 241
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
241 | Operation Mode |  | UID Ln.XYY | ON/OFF
242 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
243 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
244 | ON/OFF |  | HVAC Malfunction CD | Inhibit
245 | Filter Sign |  | Reserved | Reserved
246 | Swing
247 | Room Temperature x10 °C | RO
248 | HVAC Malfunction Code | RO
249 | Lock Bits
250 | Set Temperature Limits
251 | Reserved
252
253
254
255
256
VA number | 16 | Base Address = |  | 257
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
257 | Operation Mode |  | UID Ln.XYY | ON/OFF
258 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
259 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
260 | ON/OFF |  | HVAC Malfunction CD | Inhibit
261 | Filter Sign |  | Reserved | Reserved
262 | Swing
263 | Room Temperature x10 °C | RO
264 | HVAC Malfunction Code | RO
265 | Lock Bits
266 | Set Temperature Limits
267 | Reserved
268
269
270
271
272
VA number | 17 | Base Address = |  | 273
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
273 | Operation Mode |  | UID Ln.XYY | ON/OFF
274 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
275 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
276 | ON/OFF |  | HVAC Malfunction CD | Inhibit
277 | Filter Sign |  | Reserved | Reserved
278 | Swing
279 | Room Temperature x10 °C | RO
280 | HVAC Malfunction Code | RO
281 | Lock Bits
282 | Set Temperature Limits
283 | Reserved
284
285
286
287
288
VA number | 18 | Base Address = |  | 289
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
289 | Operation Mode |  | UID Ln.XYY | ON/OFF
290 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
291 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
292 | ON/OFF |  | HVAC Malfunction CD | Inhibit
293 | Filter Sign |  | Reserved | Reserved
294 | Swing
295 | Room Temperature x10 °C | RO
296 | HVAC Malfunction Code | RO
297 | Lock Bits
298 | Set Temperature Limits
299 | Reserved
300
301
302
303
304
VA number | 19 | Base Address = |  | 305
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
305 | Operation Mode |  | UID Ln.XYY | ON/OFF
306 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
307 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
308 | ON/OFF |  | HVAC Malfunction CD | Inhibit
309 | Filter Sign |  | Reserved | Reserved
310 | Swing
311 | Room Temperature x10 °C | RO
312 | HVAC Malfunction Code | RO
313 | Lock Bits
314 | Set Temperature Limits
315 | Reserved
316
317
318
319
320
VA number | 20 | Base Address = |  | 321
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
321 | Operation Mode |  | UID Ln.XYY | ON/OFF
322 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
323 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
324 | ON/OFF |  | HVAC Malfunction CD | Inhibit
325 | Filter Sign |  | Reserved | Reserved
326 | Swing
327 | Room Temperature x10 °C | RO
328 | HVAC Malfunction Code | RO
329 | Lock Bits
330 | Set Temperature Limits
331 | Reserved
332
333
334
335
336
VA number | 21 | Base Address = |  | 337
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
337 | Operation Mode |  | UID Ln.XYY | ON/OFF
338 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
339 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
340 | ON/OFF |  | HVAC Malfunction CD | Inhibit
341 | Filter Sign |  | Reserved | Reserved
342 | Swing
343 | Room Temperature x10 °C | RO
344 | HVAC Malfunction Code | RO
345 | Lock Bits
346 | Set Temperature Limits
347 | Reserved
348
349
350
351
352
VA number | 22 | Base Address = |  | 353
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
353 | Operation Mode |  | UID Ln.XYY | ON/OFF
354 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
355 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
356 | ON/OFF |  | HVAC Malfunction CD | Inhibit
357 | Filter Sign |  | Reserved | Reserved
358 | Swing
359 | Room Temperature x10 °C | RO
360 | HVAC Malfunction Code | RO
361 | Lock Bits
362 | Set Temperature Limits
363 | Reserved
364
365
366
367
368
VA number | 23 | Base Address = |  | 369
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
369 | Operation Mode |  | UID Ln.XYY | ON/OFF
370 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
371 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
372 | ON/OFF |  | HVAC Malfunction CD | Inhibit
373 | Filter Sign |  | Reserved | Reserved
374 | Swing
375 | Room Temperature x10 °C | RO
376 | HVAC Malfunction Code | RO
377 | Lock Bits
378 | Set Temperature Limits
379 | Reserved
380
381
382
383
384
VA number | 24 | Base Address = |  | 385
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
385 | Operation Mode |  | UID Ln.XYY | ON/OFF
386 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
387 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
388 | ON/OFF |  | HVAC Malfunction CD | Inhibit
389 | Filter Sign |  | Reserved | Reserved
390 | Swing
391 | Room Temperature x10 °C | RO
392 | HVAC Malfunction Code | RO
393 | Lock Bits
394 | Set Temperature Limits
395 | Reserved
396
397
398
399
400
VA number | 25 | Base Address = |  | 401
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
401 | Operation Mode |  | UID Ln.XYY | ON/OFF
402 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
403 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
404 | ON/OFF |  | HVAC Malfunction CD | Inhibit
405 | Filter Sign |  | Reserved | Reserved
406 | Swing
407 | Room Temperature x10 °C | RO
408 | HVAC Malfunction Code | RO
409 | Lock Bits
410 | Set Temperature Limits
411 | Reserved
412
413
414
415
416
VA number | 26 | Base Address = |  | 417
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
417 | Operation Mode |  | UID Ln.XYY | ON/OFF
418 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
419 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
420 | ON/OFF |  | HVAC Malfunction CD | Inhibit
421 | Filter Sign |  | Reserved | Reserved
422 | Swing
423 | Room Temperature x10 °C | RO
424 | HVAC Malfunction Code | RO
425 | Lock Bits
426 | Set Temperature Limits
427 | Reserved
428
429
430
431
432
VA number | 27 | Base Address = |  | 433
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
433 | Operation Mode |  | UID Ln.XYY | ON/OFF
434 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
435 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
436 | ON/OFF |  | HVAC Malfunction CD | Inhibit
437 | Filter Sign |  | Reserved | Reserved
438 | Swing
439 | Room Temperature x10 °C | RO
440 | HVAC Malfunction Code | RO
441 | Lock Bits
442 | Set Temperature Limits
443 | Reserved
444
445
446
447
448
VA number | 28 | Base Address = |  | 449
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
449 | Operation Mode |  | UID Ln.XYY | ON/OFF
450 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
451 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
452 | ON/OFF |  | HVAC Malfunction CD | Inhibit
453 | Filter Sign |  | Reserved | Reserved
454 | Swing
455 | Room Temperature x10 °C | RO
456 | HVAC Malfunction Code | RO
457 | Lock Bits
458 | Set Temperature Limits
459 | Reserved
460
461
462
463
464
VA number | 29 | Base Address = |  | 465
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
465 | Operation Mode |  | UID Ln.XYY | ON/OFF
466 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
467 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
468 | ON/OFF |  | HVAC Malfunction CD | Inhibit
469 | Filter Sign |  | Reserved | Reserved
470 | Swing
471 | Room Temperature x10 °C | RO
472 | HVAC Malfunction Code | RO
473 | Lock Bits
474 | Set Temperature Limits
475 | Reserved
476
477
478
479
480
VA number | 30 | Base Address = |  | 481
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
481 | Operation Mode |  | UID Ln.XYY | ON/OFF
482 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
483 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
484 | ON/OFF |  | HVAC Malfunction CD | Inhibit
485 | Filter Sign |  | Reserved | Reserved
486 | Swing
487 | Room Temperature x10 °C | RO
488 | HVAC Malfunction Code | RO
489 | Lock Bits
490 | Set Temperature Limits
491 | Reserved
492
493
494
495
496
VA number | 31 | Base Address = |  | 497
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
497 | Operation Mode |  | UID Ln.XYY | ON/OFF
498 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
499 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
500 | ON/OFF |  | HVAC Malfunction CD | Inhibit
501 | Filter Sign |  | Reserved | Reserved
502 | Swing
503 | Room Temperature x10 °C | RO
504 | HVAC Malfunction Code | RO
505 | Lock Bits
506 | Set Temperature Limits
507 | Reserved
508
509
510
511
512
VA number | 32 | Base Address = |  | 513
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
513 | Operation Mode |  | UID Ln.XYY | ON/OFF
514 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
515 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
516 | ON/OFF |  | HVAC Malfunction CD | Inhibit
517 | Filter Sign |  | Reserved | Reserved
518 | Swing
519 | Room Temperature x10 °C | RO
520 | HVAC Malfunction Code | RO
521 | Lock Bits
522 | Set Temperature Limits
523 | Reserved
524
525
526
527
528
VA number | 33 | Base Address = |  | 529
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
529 | Operation Mode |  | UID Ln.XYY | ON/OFF
530 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
531 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
532 | ON/OFF |  | HVAC Malfunction CD | Inhibit
533 | Filter Sign |  | Reserved | Reserved
534 | Swing
535 | Room Temperature x10 °C | RO
536 | HVAC Malfunction Code | RO
537 | Lock Bits
538 | Set Temperature Limits
539 | Reserved
540
541
542
543
544
VA number | 34 | Base Address = |  | 545
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
545 | Operation Mode |  | UID Ln.XYY | ON/OFF
546 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
547 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
548 | ON/OFF |  | HVAC Malfunction CD | Inhibit
549 | Filter Sign |  | Reserved | Reserved
550 | Swing
551 | Room Temperature x10 °C | RO
552 | HVAC Malfunction Code | RO
553 | Lock Bits
554 | Set Temperature Limits
555 | Reserved
556
557
558
559
560
VA number | 35 | Base Address = |  | 561
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
561 | Operation Mode |  | UID Ln.XYY | ON/OFF
562 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
563 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
564 | ON/OFF |  | HVAC Malfunction CD | Inhibit
565 | Filter Sign |  | Reserved | Reserved
566 | Swing
567 | Room Temperature x10 °C | RO
568 | HVAC Malfunction Code | RO
569 | Lock Bits
570 | Set Temperature Limits
571 | Reserved
572
573
574
575
576
VA number | 36 | Base Address = |  | 577
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
577 | Operation Mode |  | UID Ln.XYY | ON/OFF
578 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
579 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
580 | ON/OFF |  | HVAC Malfunction CD | Inhibit
581 | Filter Sign |  | Reserved | Reserved
582 | Swing
583 | Room Temperature x10 °C | RO
584 | HVAC Malfunction Code | RO
585 | Lock Bits
586 | Set Temperature Limits
587 | Reserved
588
589
590
591
592
VA number | 37 | Base Address = |  | 593
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
593 | Operation Mode |  | UID Ln.XYY | ON/OFF
594 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
595 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
596 | ON/OFF |  | HVAC Malfunction CD | Inhibit
597 | Filter Sign |  | Reserved | Reserved
598 | Swing
599 | Room Temperature x10 °C | RO
600 | HVAC Malfunction Code | RO
601 | Lock Bits
602 | Set Temperature Limits
603 | Reserved
604
605
606
607
608
VA number | 38 | Base Address = |  | 609
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
609 | Operation Mode |  | UID Ln.XYY | ON/OFF
610 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
611 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
612 | ON/OFF |  | HVAC Malfunction CD | Inhibit
613 | Filter Sign |  | Reserved | Reserved
614 | Swing
615 | Room Temperature x10 °C | RO
616 | HVAC Malfunction Code | RO
617 | Lock Bits
618 | Set Temperature Limits
619 | Reserved
620
621
622
623
624
VA number | 39 | Base Address = |  | 625
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
625 | Operation Mode |  | UID Ln.XYY | ON/OFF
626 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
627 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
628 | ON/OFF |  | HVAC Malfunction CD | Inhibit
629 | Filter Sign |  | Reserved | Reserved
630 | Swing
631 | Room Temperature x10 °C | RO
632 | HVAC Malfunction Code | RO
633 | Lock Bits
634 | Set Temperature Limits
635 | Reserved
636
637
638
639
640
VA number | 40 | Base Address = |  | 641
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
641 | Operation Mode |  | UID Ln.XYY | ON/OFF
642 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
643 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
644 | ON/OFF |  | HVAC Malfunction CD | Inhibit
645 | Filter Sign |  | Reserved | Reserved
646 | Swing
647 | Room Temperature x10 °C | RO
648 | HVAC Malfunction Code | RO
649 | Lock Bits
650 | Set Temperature Limits
651 | Reserved
652
653
654
655
656
VA number | 41 | Base Address = |  | 657
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
657 | Operation Mode |  | UID Ln.XYY | ON/OFF
658 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
659 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
660 | ON/OFF |  | HVAC Malfunction CD | Inhibit
661 | Filter Sign |  | Reserved | Reserved
662 | Swing
663 | Room Temperature x10 °C | RO
664 | HVAC Malfunction Code | RO
665 | Lock Bits
666 | Set Temperature Limits
667 | Reserved
668
669
670
671
672
VA number | 42 | Base Address = |  | 673
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
673 | Operation Mode |  | UID Ln.XYY | ON/OFF
674 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
675 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
676 | ON/OFF |  | HVAC Malfunction CD | Inhibit
677 | Filter Sign |  | Reserved | Reserved
678 | Swing
679 | Room Temperature x10 °C | RO
680 | HVAC Malfunction Code | RO
681 | Lock Bits
682 | Set Temperature Limits
683 | Reserved
684
685
686
687
688
VA number | 43 | Base Address = |  | 689
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
689 | Operation Mode |  | UID Ln.XYY | ON/OFF
690 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
691 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
692 | ON/OFF |  | HVAC Malfunction CD | Inhibit
693 | Filter Sign |  | Reserved | Reserved
694 | Swing
695 | Room Temperature x10 °C | RO
696 | HVAC Malfunction Code | RO
697 | Lock Bits
698 | Set Temperature Limits
699 | Reserved
700
701
702
703
704
VA number | 44 | Base Address = |  | 705
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
705 | Operation Mode |  | UID Ln.XYY | ON/OFF
706 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
707 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
708 | ON/OFF |  | HVAC Malfunction CD | Inhibit
709 | Filter Sign |  | Reserved | Reserved
710 | Swing
711 | Room Temperature x10 °C | RO
712 | HVAC Malfunction Code | RO
713 | Lock Bits
714 | Set Temperature Limits
715 | Reserved
716
717
718
719
720
VA number | 45 | Base Address = |  | 721
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
721 | Operation Mode |  | UID Ln.XYY | ON/OFF
722 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
723 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
724 | ON/OFF |  | HVAC Malfunction CD | Inhibit
725 | Filter Sign |  | Reserved | Reserved
726 | Swing
727 | Room Temperature x10 °C | RO
728 | HVAC Malfunction Code | RO
729 | Lock Bits
730 | Set Temperature Limits
731 | Reserved
732
733
734
735
736
VA number | 46 | Base Address = |  | 737
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
737 | Operation Mode |  | UID Ln.XYY | ON/OFF
738 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
739 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
740 | ON/OFF |  | HVAC Malfunction CD | Inhibit
741 | Filter Sign |  | Reserved | Reserved
742 | Swing
743 | Room Temperature x10 °C | RO
744 | HVAC Malfunction Code | RO
745 | Lock Bits
746 | Set Temperature Limits
747 | Reserved
748
749
750
751
752
VA number | 47 | Base Address = |  | 753
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
753 | Operation Mode |  | UID Ln.XYY | ON/OFF
754 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
755 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
756 | ON/OFF |  | HVAC Malfunction CD | Inhibit
757 | Filter Sign |  | Reserved | Reserved
758 | Swing
759 | Room Temperature x10 °C | RO
760 | HVAC Malfunction Code | RO
761 | Lock Bits
762 | Set Temperature Limits
763 | Reserved
764
765
766
767
768
VA number | 48 | Base Address = |  | 769
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
769 | Operation Mode |  | UID Ln.XYY | ON/OFF
770 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
771 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
772 | ON/OFF |  | HVAC Malfunction CD | Inhibit
773 | Filter Sign |  | Reserved | Reserved
774 | Swing
775 | Room Temperature x10 °C | RO
776 | HVAC Malfunction Code | RO
777 | Lock Bits
778 | Set Temperature Limits
779 | Reserved
780
781
782
783
784
VA number | 49 | Base Address = |  | 785
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
785 | Operation Mode |  | UID Ln.XYY | ON/OFF
786 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
787 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
788 | ON/OFF |  | HVAC Malfunction CD | Inhibit
789 | Filter Sign |  | Reserved | Reserved
790 | Swing
791 | Room Temperature x10 °C | RO
792 | HVAC Malfunction Code | RO
793 | Lock Bits
794 | Set Temperature Limits
795 | Reserved
796
797
798
799
800
VA number | 50 | Base Address = |  | 801
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
801 | Operation Mode |  | UID Ln.XYY | ON/OFF
802 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
803 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
804 | ON/OFF |  | HVAC Malfunction CD | Inhibit
805 | Filter Sign |  | Reserved | Reserved
806 | Swing
807 | Room Temperature x10 °C | RO
808 | HVAC Malfunction Code | RO
809 | Lock Bits
810 | Set Temperature Limits
811 | Reserved
812
813
814
815
816
VA number | 51 | Base Address = |  | 817
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
817 | Operation Mode |  | UID Ln.XYY | ON/OFF
818 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
819 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
820 | ON/OFF |  | HVAC Malfunction CD | Inhibit
821 | Filter Sign |  | Reserved | Reserved
822 | Swing
823 | Room Temperature x10 °C | RO
824 | HVAC Malfunction Code | RO
825 | Lock Bits
826 | Set Temperature Limits
827 | Reserved
828
829
830
831
832
VA number | 52 | Base Address = |  | 833
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
833 | Operation Mode |  | UID Ln.XYY | ON/OFF
834 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
835 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
836 | ON/OFF |  | HVAC Malfunction CD | Inhibit
837 | Filter Sign |  | Reserved | Reserved
838 | Swing
839 | Room Temperature x10 °C | RO
840 | HVAC Malfunction Code | RO
841 | Lock Bits
842 | Set Temperature Limits
843 | Reserved
844
845
846
847
848
VA number | 53 | Base Address = |  | 849
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
849 | Operation Mode |  | UID Ln.XYY | ON/OFF
850 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
851 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
852 | ON/OFF |  | HVAC Malfunction CD | Inhibit
853 | Filter Sign |  | Reserved | Reserved
854 | Swing
855 | Room Temperature x10 °C | RO
856 | HVAC Malfunction Code | RO
857 | Lock Bits
858 | Set Temperature Limits
859 | Reserved
860
861
862
863
864
VA number | 54 | Base Address = |  | 865
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
865 | Operation Mode |  | UID Ln.XYY | ON/OFF
866 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
867 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
868 | ON/OFF |  | HVAC Malfunction CD | Inhibit
869 | Filter Sign |  | Reserved | Reserved
870 | Swing
871 | Room Temperature x10 °C | RO
872 | HVAC Malfunction Code | RO
873 | Lock Bits
874 | Set Temperature Limits
875 | Reserved
876
877
878
879
880
VA number | 55 | Base Address = |  | 881
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
881 | Operation Mode |  | UID Ln.XYY | ON/OFF
882 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
883 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
884 | ON/OFF |  | HVAC Malfunction CD | Inhibit
885 | Filter Sign |  | Reserved | Reserved
886 | Swing
887 | Room Temperature x10 °C | RO
888 | HVAC Malfunction Code | RO
889 | Lock Bits
890 | Set Temperature Limits
891 | Reserved
892
893
894
895
896
VA number | 56 | Base Address = |  | 897
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
897 | Operation Mode |  | UID Ln.XYY | ON/OFF
898 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
899 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
900 | ON/OFF |  | HVAC Malfunction CD | Inhibit
901 | Filter Sign |  | Reserved | Reserved
902 | Swing
903 | Room Temperature x10 °C | RO
904 | HVAC Malfunction Code | RO
905 | Lock Bits
906 | Set Temperature Limits
907 | Reserved
908
909
910
911
912
VA number | 57 | Base Address = |  | 913
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
913 | Operation Mode |  | UID Ln.XYY | ON/OFF
914 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
915 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
916 | ON/OFF |  | HVAC Malfunction CD | Inhibit
917 | Filter Sign |  | Reserved | Reserved
918 | Swing
919 | Room Temperature x10 °C | RO
920 | HVAC Malfunction Code | RO
921 | Lock Bits
922 | Set Temperature Limits
923 | Reserved
924
925
926
927
928
VA number | 58 | Base Address = |  | 929
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
929 | Operation Mode |  | UID Ln.XYY | ON/OFF
930 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
931 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
932 | ON/OFF |  | HVAC Malfunction CD | Inhibit
933 | Filter Sign |  | Reserved | Reserved
934 | Swing
935 | Room Temperature x10 °C | RO
936 | HVAC Malfunction Code | RO
937 | Lock Bits
938 | Set Temperature Limits
939 | Reserved
940
941
942
943
944
VA number | 59 | Base Address = |  | 945
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
945 | Operation Mode |  | UID Ln.XYY | ON/OFF
946 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
947 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
948 | ON/OFF |  | HVAC Malfunction CD | Inhibit
949 | Filter Sign |  | Reserved | Reserved
950 | Swing
951 | Room Temperature x10 °C | RO
952 | HVAC Malfunction Code | RO
953 | Lock Bits
954 | Set Temperature Limits
955 | Reserved
956
957
958
959
960
VA number | 60 | Base Address = |  | 961
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
961 | Operation Mode |  | UID Ln.XYY | ON/OFF
962 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
963 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
964 | ON/OFF |  | HVAC Malfunction CD | Inhibit
965 | Filter Sign |  | Reserved | Reserved
966 | Swing
967 | Room Temperature x10 °C | RO
968 | HVAC Malfunction Code | RO
969 | Lock Bits
970 | Set Temperature Limits
971 | Reserved
972
973
974
975
976
VA number | 61 | Base Address = |  | 977
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
977 | Operation Mode |  | UID Ln.XYY | ON/OFF
978 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
979 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
980 | ON/OFF |  | HVAC Malfunction CD | Inhibit
981 | Filter Sign |  | Reserved | Reserved
982 | Swing
983 | Room Temperature x10 °C | RO
984 | HVAC Malfunction Code | RO
985 | Lock Bits
986 | Set Temperature Limits
987 | Reserved
988
989
990
991
992
VA number | 62 | Base Address = |  | 993
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
993 | Operation Mode |  | UID Ln.XYY | ON/OFF
994 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
995 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
996 | ON/OFF |  | HVAC Malfunction CD | Inhibit
997 | Filter Sign |  | Reserved | Reserved
998 | Swing
999 | Room Temperature x10 °C | RO
1000 | HVAC Malfunction Code | RO
1001 | Lock Bits
1002 | Set Temperature Limits
1003 | Reserved
1004
1005
1006
1007
1008
VA number | 63 | Base Address = |  | 1009
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1009 | Operation Mode |  | UID Ln.XYY | ON/OFF
1010 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1011 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1012 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1013 | Filter Sign |  | Reserved | Reserved
1014 | Swing
1015 | Room Temperature x10 °C | RO
1016 | HVAC Malfunction Code | RO
1017 | Lock Bits
1018 | Set Temperature Limits
1019 | Reserved
1020
1021
1022
1023
1024
VA number | 64 | Base Address = |  | 1025
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1025 | Operation Mode |  | UID Ln.XYY | ON/OFF
1026 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1027 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1028 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1029 | Filter Sign |  | Reserved | Reserved
1030 | Swing
1031 | Room Temperature x10 °C | RO
1032 | HVAC Malfunction Code | RO
1033 | Lock Bits
1034 | Set Temperature Limits
1035 | Reserved
1036
1037
1038
1039
1040
VA number | 65 | Base Address = |  | 1041
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1041 | Operation Mode |  | UID Ln.XYY | ON/OFF
1042 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1043 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1044 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1045 | Filter Sign |  | Reserved | Reserved
1046 | Swing
1047 | Room Temperature x10 °C | RO
1048 | HVAC Malfunction Code | RO
1049 | Lock Bits
1050 | Set Temperature Limits
1051 | Reserved
1052
1053
1054
1055
1056
VA number | 66 | Base Address = |  | 1057
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1057 | Operation Mode |  | UID Ln.XYY | ON/OFF
1058 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1059 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1060 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1061 | Filter Sign |  | Reserved | Reserved
1062 | Swing
1063 | Room Temperature x10 °C | RO
1064 | HVAC Malfunction Code | RO
1065 | Lock Bits
1066 | Set Temperature Limits
1067 | Reserved
1068
1069
1070
1071
1072
VA number | 67 | Base Address = |  | 1073
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1073 | Operation Mode |  | UID Ln.XYY | ON/OFF
1074 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1075 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1076 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1077 | Filter Sign |  | Reserved | Reserved
1078 | Swing
1079 | Room Temperature x10 °C | RO
1080 | HVAC Malfunction Code | RO
1081 | Lock Bits
1082 | Set Temperature Limits
1083 | Reserved
1084
1085
1086
1087
1088
VA number | 68 | Base Address = |  | 1089
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1089 | Operation Mode |  | UID Ln.XYY | ON/OFF
1090 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1091 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1092 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1093 | Filter Sign |  | Reserved | Reserved
1094 | Swing
1095 | Room Temperature x10 °C | RO
1096 | HVAC Malfunction Code | RO
1097 | Lock Bits
1098 | Set Temperature Limits
1099 | Reserved
1100
1101
1102
1103
1104
VA number | 69 | Base Address = |  | 1105
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1105 | Operation Mode |  | UID Ln.XYY | ON/OFF
1106 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1107 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1108 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1109 | Filter Sign |  | Reserved | Reserved
1110 | Swing
1111 | Room Temperature x10 °C | RO
1112 | HVAC Malfunction Code | RO
1113 | Lock Bits
1114 | Set Temperature Limits
1115 | Reserved
1116
1117
1118
1119
1120
VA number | 70 | Base Address = |  | 1121
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1121 | Operation Mode |  | UID Ln.XYY | ON/OFF
1122 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1123 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1124 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1125 | Filter Sign |  | Reserved | Reserved
1126 | Swing
1127 | Room Temperature x10 °C | RO
1128 | HVAC Malfunction Code | RO
1129 | Lock Bits
1130 | Set Temperature Limits
1131 | Reserved
1132
1133
1134
1135
1136
VA number | 71 | Base Address = |  | 1137
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1137 | Operation Mode |  | UID Ln.XYY | ON/OFF
1138 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1139 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1140 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1141 | Filter Sign |  | Reserved | Reserved
1142 | Swing
1143 | Room Temperature x10 °C | RO
1144 | HVAC Malfunction Code | RO
1145 | Lock Bits
1146 | Set Temperature Limits
1147 | Reserved
1148
1149
1150
1151
1152
VA number | 72 | Base Address = |  | 1153
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1153 | Operation Mode |  | UID Ln.XYY | ON/OFF
1154 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1155 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1156 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1157 | Filter Sign |  | Reserved | Reserved
1158 | Swing
1159 | Room Temperature x10 °C | RO
1160 | HVAC Malfunction Code | RO
1161 | Lock Bits
1162 | Set Temperature Limits
1163 | Reserved
1164
1165
1166
1167
1168
VA number | 73 | Base Address = |  | 1169
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1169 | Operation Mode |  | UID Ln.XYY | ON/OFF
1170 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1171 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1172 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1173 | Filter Sign |  | Reserved | Reserved
1174 | Swing
1175 | Room Temperature x10 °C | RO
1176 | HVAC Malfunction Code | RO
1177 | Lock Bits
1178 | Set Temperature Limits
1179 | Reserved
1180
1181
1182
1183
1184
VA number | 74 | Base Address = |  | 1185
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1185 | Operation Mode |  | UID Ln.XYY | ON/OFF
1186 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1187 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1188 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1189 | Filter Sign |  | Reserved | Reserved
1190 | Swing
1191 | Room Temperature x10 °C | RO
1192 | HVAC Malfunction Code | RO
1193 | Lock Bits
1194 | Set Temperature Limits
1195 | Reserved
1196
1197
1198
1199
1200
VA number | 75 | Base Address = |  | 1201
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1201 | Operation Mode |  | UID Ln.XYY | ON/OFF
1202 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1203 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1204 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1205 | Filter Sign |  | Reserved | Reserved
1206 | Swing
1207 | Room Temperature x10 °C | RO
1208 | HVAC Malfunction Code | RO
1209 | Lock Bits
1210 | Set Temperature Limits
1211 | Reserved
1212
1213
1214
1215
1216
VA number | 76 | Base Address = |  | 1217
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1217 | Operation Mode |  | UID Ln.XYY | ON/OFF
1218 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1219 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1220 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1221 | Filter Sign |  | Reserved | Reserved
1222 | Swing
1223 | Room Temperature x10 °C | RO
1224 | HVAC Malfunction Code | RO
1225 | Lock Bits
1226 | Set Temperature Limits
1227 | Reserved
1228
1229
1230
1231
1232
VA number | 77 | Base Address = |  | 1233
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1233 | Operation Mode |  | UID Ln.XYY | ON/OFF
1234 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1235 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1236 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1237 | Filter Sign |  | Reserved | Reserved
1238 | Swing
1239 | Room Temperature x10 °C | RO
1240 | HVAC Malfunction Code | RO
1241 | Lock Bits
1242 | Set Temperature Limits
1243 | Reserved
1244
1245
1246
1247
1248
VA number | 78 | Base Address = |  | 1249
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1249 | Operation Mode |  | UID Ln.XYY | ON/OFF
1250 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1251 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1252 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1253 | Filter Sign |  | Reserved | Reserved
1254 | Swing
1255 | Room Temperature x10 °C | RO
1256 | HVAC Malfunction Code | RO
1257 | Lock Bits
1258 | Set Temperature Limits
1259 | Reserved
1260
1261
1262
1263
1264
VA number | 79 | Base Address = |  | 1265
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1265 | Operation Mode |  | UID Ln.XYY | ON/OFF
1266 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1267 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1268 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1269 | Filter Sign |  | Reserved | Reserved
1270 | Swing
1271 | Room Temperature x10 °C | RO
1272 | HVAC Malfunction Code | RO
1273 | Lock Bits
1274 | Set Temperature Limits
1275 | Reserved
1276
1277
1278
1279
1280
VA number | 80 | Base Address = |  | 1281
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1281 | Operation Mode |  | UID Ln.XYY | ON/OFF
1282 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1283 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1284 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1285 | Filter Sign |  | Reserved | Reserved
1286 | Swing
1287 | Room Temperature x10 °C | RO
1288 | HVAC Malfunction Code | RO
1289 | Lock Bits
1290 | Set Temperature Limits
1291 | Reserved
1292
1293
1294
1295
1296
VA number | 81 | Base Address = |  | 1297
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1297 | Operation Mode |  | UID Ln.XYY | ON/OFF
1298 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1299 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1300 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1301 | Filter Sign |  | Reserved | Reserved
1302 | Swing
1303 | Room Temperature x10 °C | RO
1304 | HVAC Malfunction Code | RO
1305 | Lock Bits
1306 | Set Temperature Limits
1307 | Reserved
1308
1309
1310
1311
1312
VA number | 82 | Base Address = |  | 1313
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1313 | Operation Mode |  | UID Ln.XYY | ON/OFF
1314 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1315 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1316 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1317 | Filter Sign |  | Reserved | Reserved
1318 | Swing
1319 | Room Temperature x10 °C | RO
1320 | HVAC Malfunction Code | RO
1321 | Lock Bits
1322 | Set Temperature Limits
1323 | Reserved
1324
1325
1326
1327
1328
VA number | 83 | Base Address = |  | 1329
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1329 | Operation Mode |  | UID Ln.XYY | ON/OFF
1330 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1331 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1332 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1333 | Filter Sign |  | Reserved | Reserved
1334 | Swing
1335 | Room Temperature x10 °C | RO
1336 | HVAC Malfunction Code | RO
1337 | Lock Bits
1338 | Set Temperature Limits
1339 | Reserved
1340
1341
1342
1343
1344
VA number | 84 | Base Address = |  | 1345
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1345 | Operation Mode |  | UID Ln.XYY | ON/OFF
1346 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1347 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1348 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1349 | Filter Sign |  | Reserved | Reserved
1350 | Swing
1351 | Room Temperature x10 °C | RO
1352 | HVAC Malfunction Code | RO
1353 | Lock Bits
1354 | Set Temperature Limits
1355 | Reserved
1356
1357
1358
1359
1360
VA number | 85 | Base Address = |  | 1361
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1361 | Operation Mode |  | UID Ln.XYY | ON/OFF
1362 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1363 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1364 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1365 | Filter Sign |  | Reserved | Reserved
1366 | Swing
1367 | Room Temperature x10 °C | RO
1368 | HVAC Malfunction Code | RO
1369 | Lock Bits
1370 | Set Temperature Limits
1371 | Reserved
1372
1373
1374
1375
1376
VA number | 86 | Base Address = |  | 1377
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1377 | Operation Mode |  | UID Ln.XYY | ON/OFF
1378 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1379 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1380 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1381 | Filter Sign |  | Reserved | Reserved
1382 | Swing
1383 | Room Temperature x10 °C | RO
1384 | HVAC Malfunction Code | RO
1385 | Lock Bits
1386 | Set Temperature Limits
1387 | Reserved
1388
1389
1390
1391
1392
VA number | 87 | Base Address = |  | 1393
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1393 | Operation Mode |  | UID Ln.XYY | ON/OFF
1394 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1395 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1396 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1397 | Filter Sign |  | Reserved | Reserved
1398 | Swing
1399 | Room Temperature x10 °C | RO
1400 | HVAC Malfunction Code | RO
1401 | Lock Bits
1402 | Set Temperature Limits
1403 | Reserved
1404
1405
1406
1407
1408
VA number | 88 | Base Address = |  | 1409
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1409 | Operation Mode |  | UID Ln.XYY | ON/OFF
1410 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1411 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1412 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1413 | Filter Sign |  | Reserved | Reserved
1414 | Swing
1415 | Room Temperature x10 °C | RO
1416 | HVAC Malfunction Code | RO
1417 | Lock Bits
1418 | Set Temperature Limits
1419 | Reserved
1420
1421
1422
1423
1424
VA number | 89 | Base Address = |  | 1425
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1425 | Operation Mode |  | UID Ln.XYY | ON/OFF
1426 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1427 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1428 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1429 | Filter Sign |  | Reserved | Reserved
1430 | Swing
1431 | Room Temperature x10 °C | RO
1432 | HVAC Malfunction Code | RO
1433 | Lock Bits
1434 | Set Temperature Limits
1435 | Reserved
1436
1437
1438
1439
1440
VA number | 90 | Base Address = |  | 1441
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1441 | Operation Mode |  | UID Ln.XYY | ON/OFF
1442 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1443 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1444 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1445 | Filter Sign |  | Reserved | Reserved
1446 | Swing
1447 | Room Temperature x10 °C | RO
1448 | HVAC Malfunction Code | RO
1449 | Lock Bits
1450 | Set Temperature Limits
1451 | Reserved
1452
1453
1454
1455
1456
VA number | 91 | Base Address = |  | 1457
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1457 | Operation Mode |  | UID Ln.XYY | ON/OFF
1458 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1459 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1460 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1461 | Filter Sign |  | Reserved | Reserved
1462 | Swing
1463 | Room Temperature x10 °C | RO
1464 | HVAC Malfunction Code | RO
1465 | Lock Bits
1466 | Set Temperature Limits
1467 | Reserved
1468
1469
1470
1471
1472
VA number | 92 | Base Address = |  | 1473
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1473 | Operation Mode |  | UID Ln.XYY | ON/OFF
1474 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1475 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1476 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1477 | Filter Sign |  | Reserved | Reserved
1478 | Swing
1479 | Room Temperature x10 °C | RO
1480 | HVAC Malfunction Code | RO
1481 | Lock Bits
1482 | Set Temperature Limits
1483 | Reserved
1484
1485
1486
1487
1488
VA number | 93 | Base Address = |  | 1489
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1489 | Operation Mode |  | UID Ln.XYY | ON/OFF
1490 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1491 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1492 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1493 | Filter Sign |  | Reserved | Reserved
1494 | Swing
1495 | Room Temperature x10 °C | RO
1496 | HVAC Malfunction Code | RO
1497 | Lock Bits
1498 | Set Temperature Limits
1499 | Reserved
1500
1501
1502
1503
1504
VA number | 94 | Base Address = |  | 1505
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1505 | Operation Mode |  | UID Ln.XYY | ON/OFF
1506 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1507 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1508 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1509 | Filter Sign |  | Reserved | Reserved
1510 | Swing
1511 | Room Temperature x10 °C | RO
1512 | HVAC Malfunction Code | RO
1513 | Lock Bits
1514 | Set Temperature Limits
1515 | Reserved
1516
1517
1518
1519
1520
VA number | 95 | Base Address = |  | 1521
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1521 | Operation Mode |  | UID Ln.XYY | ON/OFF
1522 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1523 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1524 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1525 | Filter Sign |  | Reserved | Reserved
1526 | Swing
1527 | Room Temperature x10 °C | RO
1528 | HVAC Malfunction Code | RO
1529 | Lock Bits
1530 | Set Temperature Limits
1531 | Reserved
1532
1533
1534
1535
1536
VA number | 96 | Base Address = |  | 1537
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1537 | Operation Mode |  | UID Ln.XYY | ON/OFF
1538 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1539 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1540 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1541 | Filter Sign |  | Reserved | Reserved
1542 | Swing
1543 | Room Temperature x10 °C | RO
1544 | HVAC Malfunction Code | RO
1545 | Lock Bits
1546 | Set Temperature Limits
1547 | Reserved
1548
1549
1550
1551
1552
VA number | 97 | Base Address = |  | 1553
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1553 | Operation Mode |  | UID Ln.XYY | ON/OFF
1554 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1555 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1556 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1557 | Filter Sign |  | Reserved | Reserved
1558 | Swing
1559 | Room Temperature x10 °C | RO
1560 | HVAC Malfunction Code | RO
1561 | Lock Bits
1562 | Set Temperature Limits
1563 | Reserved
1564
1565
1566
1567
1568
VA number | 98 | Base Address = |  | 1569
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1569 | Operation Mode |  | UID Ln.XYY | ON/OFF
1570 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1571 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1572 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1573 | Filter Sign |  | Reserved | Reserved
1574 | Swing
1575 | Room Temperature x10 °C | RO
1576 | HVAC Malfunction Code | RO
1577 | Lock Bits
1578 | Set Temperature Limits
1579 | Reserved
1580
1581
1582
1583
1584
VA number | 99 | Base Address = |  | 1585
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1585 | Operation Mode |  | UID Ln.XYY | ON/OFF
1586 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1587 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1588 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1589 | Filter Sign |  | Reserved | Reserved
1590 | Swing
1591 | Room Temperature x10 °C | RO
1592 | HVAC Malfunction Code | RO
1593 | Lock Bits
1594 | Set Temperature Limits
1595 | Reserved
1596
1597
1598
1599
1600
VA number | 100 | Base Address = |  | 1601
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1601 | Operation Mode |  | UID Ln.XYY | ON/OFF
1602 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1603 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1604 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1605 | Filter Sign |  | Reserved | Reserved
1606 | Swing
1607 | Room Temperature x10 °C | RO
1608 | HVAC Malfunction Code | RO
1609 | Lock Bits
1610 | Set Temperature Limits
1611 | Reserved
1612
1613
1614
1615
1616
VA number | 101 | Base Address = |  | 1617
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1617 | Operation Mode |  | UID Ln.XYY | ON/OFF
1618 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1619 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1620 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1621 | Filter Sign |  | Reserved | Reserved
1622 | Swing
1623 | Room Temperature x10 °C | RO
1624 | HVAC Malfunction Code | RO
1625 | Lock Bits
1626 | Set Temperature Limits
1627 | Reserved
1628
1629
1630
1631
1632
VA number | 102 | Base Address = |  | 1633
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1633 | Operation Mode |  | UID Ln.XYY | ON/OFF
1634 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1635 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1636 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1637 | Filter Sign |  | Reserved | Reserved
1638 | Swing
1639 | Room Temperature x10 °C | RO
1640 | HVAC Malfunction Code | RO
1641 | Lock Bits
1642 | Set Temperature Limits
1643 | Reserved
1644
1645
1646
1647
1648
VA number | 103 | Base Address = |  | 1649
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1649 | Operation Mode |  | UID Ln.XYY | ON/OFF
1650 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1651 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1652 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1653 | Filter Sign |  | Reserved | Reserved
1654 | Swing
1655 | Room Temperature x10 °C | RO
1656 | HVAC Malfunction Code | RO
1657 | Lock Bits
1658 | Set Temperature Limits
1659 | Reserved
1660
1661
1662
1663
1664
VA number | 104 | Base Address = |  | 1665
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1665 | Operation Mode |  | UID Ln.XYY | ON/OFF
1666 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1667 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1668 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1669 | Filter Sign |  | Reserved | Reserved
1670 | Swing
1671 | Room Temperature x10 °C | RO
1672 | HVAC Malfunction Code | RO
1673 | Lock Bits
1674 | Set Temperature Limits
1675 | Reserved
1676
1677
1678
1679
1680
VA number | 105 | Base Address = |  | 1681
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1681 | Operation Mode |  | UID Ln.XYY | ON/OFF
1682 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1683 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1684 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1685 | Filter Sign |  | Reserved | Reserved
1686 | Swing
1687 | Room Temperature x10 °C | RO
1688 | HVAC Malfunction Code | RO
1689 | Lock Bits
1690 | Set Temperature Limits
1691 | Reserved
1692
1693
1694
1695
1696
VA number | 106 | Base Address = |  | 1697
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1697 | Operation Mode |  | UID Ln.XYY | ON/OFF
1698 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1699 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1700 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1701 | Filter Sign |  | Reserved | Reserved
1702 | Swing
1703 | Room Temperature x10 °C | RO
1704 | HVAC Malfunction Code | RO
1705 | Lock Bits
1706 | Set Temperature Limits
1707 | Reserved
1708
1709
1710
1711
1712
VA number | 107 | Base Address = |  | 1713
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1713 | Operation Mode |  | UID Ln.XYY | ON/OFF
1714 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1715 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1716 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1717 | Filter Sign |  | Reserved | Reserved
1718 | Swing
1719 | Room Temperature x10 °C | RO
1720 | HVAC Malfunction Code | RO
1721 | Lock Bits
1722 | Set Temperature Limits
1723 | Reserved
1724
1725
1726
1727
1728
VA number | 108 | Base Address = |  | 1729
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1729 | Operation Mode |  | UID Ln.XYY | ON/OFF
1730 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1731 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1732 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1733 | Filter Sign |  | Reserved | Reserved
1734 | Swing
1735 | Room Temperature x10 °C | RO
1736 | HVAC Malfunction Code | RO
1737 | Lock Bits
1738 | Set Temperature Limits
1739 | Reserved
1740
1741
1742
1743
1744
VA number | 109 | Base Address = |  | 1745
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1745 | Operation Mode |  | UID Ln.XYY | ON/OFF
1746 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1747 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1748 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1749 | Filter Sign |  | Reserved | Reserved
1750 | Swing
1751 | Room Temperature x10 °C | RO
1752 | HVAC Malfunction Code | RO
1753 | Lock Bits
1754 | Set Temperature Limits
1755 | Reserved
1756
1757
1758
1759
1760
VA number | 110 | Base Address = |  | 1761
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1761 | Operation Mode |  | UID Ln.XYY | ON/OFF
1762 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1763 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1764 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1765 | Filter Sign |  | Reserved | Reserved
1766 | Swing
1767 | Room Temperature x10 °C | RO
1768 | HVAC Malfunction Code | RO
1769 | Lock Bits
1770 | Set Temperature Limits
1771 | Reserved
1772
1773
1774
1775
1776
VA number | 111 | Base Address = |  | 1777
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1777 | Operation Mode |  | UID Ln.XYY | ON/OFF
1778 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1779 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1780 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1781 | Filter Sign |  | Reserved | Reserved
1782 | Swing
1783 | Room Temperature x10 °C | RO
1784 | HVAC Malfunction Code | RO
1785 | Lock Bits
1786 | Set Temperature Limits
1787 | Reserved
1788
1789
1790
1791
1792
VA number | 112 | Base Address = |  | 1793
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1793 | Operation Mode |  | UID Ln.XYY | ON/OFF
1794 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1795 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1796 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1797 | Filter Sign |  | Reserved | Reserved
1798 | Swing
1799 | Room Temperature x10 °C | RO
1800 | HVAC Malfunction Code | RO
1801 | Lock Bits
1802 | Set Temperature Limits
1803 | Reserved
1804
1805
1806
1807
1808
VA number | 113 | Base Address = |  | 1809
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1809 | Operation Mode |  | UID Ln.XYY | ON/OFF
1810 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1811 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1812 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1813 | Filter Sign |  | Reserved | Reserved
1814 | Swing
1815 | Room Temperature x10 °C | RO
1816 | HVAC Malfunction Code | RO
1817 | Lock Bits
1818 | Set Temperature Limits
1819 | Reserved
1820
1821
1822
1823
1824
VA number | 114 | Base Address = |  | 1825
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1825 | Operation Mode |  | UID Ln.XYY | ON/OFF
1826 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1827 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1828 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1829 | Filter Sign |  | Reserved | Reserved
1830 | Swing
1831 | Room Temperature x10 °C | RO
1832 | HVAC Malfunction Code | RO
1833 | Lock Bits
1834 | Set Temperature Limits
1835 | Reserved
1836
1837
1838
1839
1840
VA number | 115 | Base Address = |  | 1841
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1841 | Operation Mode |  | UID Ln.XYY | ON/OFF
1842 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1843 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1844 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1845 | Filter Sign |  | Reserved | Reserved
1846 | Swing
1847 | Room Temperature x10 °C | RO
1848 | HVAC Malfunction Code | RO
1849 | Lock Bits
1850 | Set Temperature Limits
1851 | Reserved
1852
1853
1854
1855
1856
VA number | 116 | Base Address = |  | 1857
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1857 | Operation Mode |  | UID Ln.XYY | ON/OFF
1858 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1859 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1860 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1861 | Filter Sign |  | Reserved | Reserved
1862 | Swing
1863 | Room Temperature x10 °C | RO
1864 | HVAC Malfunction Code | RO
1865 | Lock Bits
1866 | Set Temperature Limits
1867 | Reserved
1868
1869
1870
1871
1872
VA number | 117 | Base Address = |  | 1873
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1873 | Operation Mode |  | UID Ln.XYY | ON/OFF
1874 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1875 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1876 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1877 | Filter Sign |  | Reserved | Reserved
1878 | Swing
1879 | Room Temperature x10 °C | RO
1880 | HVAC Malfunction Code | RO
1881 | Lock Bits
1882 | Set Temperature Limits
1883 | Reserved
1884
1885
1886
1887
1888
VA number | 118 | Base Address = |  | 1889
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1889 | Operation Mode |  | UID Ln.XYY | ON/OFF
1890 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1891 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1892 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1893 | Filter Sign |  | Reserved | Reserved
1894 | Swing
1895 | Room Temperature x10 °C | RO
1896 | HVAC Malfunction Code | RO
1897 | Lock Bits
1898 | Set Temperature Limits
1899 | Reserved
1900
1901
1902
1903
1904
VA number | 119 | Base Address = |  | 1905
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1905 | Operation Mode |  | UID Ln.XYY | ON/OFF
1906 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1907 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1908 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1909 | Filter Sign |  | Reserved | Reserved
1910 | Swing
1911 | Room Temperature x10 °C | RO
1912 | HVAC Malfunction Code | RO
1913 | Lock Bits
1914 | Set Temperature Limits
1915 | Reserved
1916
1917
1918
1919
1920
VA number | 120 | Base Address = |  | 1921
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1921 | Operation Mode |  | UID Ln.XYY | ON/OFF
1922 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1923 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1924 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1925 | Filter Sign |  | Reserved | Reserved
1926 | Swing
1927 | Room Temperature x10 °C | RO
1928 | HVAC Malfunction Code | RO
1929 | Lock Bits
1930 | Set Temperature Limits
1931 | Reserved
1932
1933
1934
1935
1936
VA number | 121 | Base Address = |  | 1937
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1937 | Operation Mode |  | UID Ln.XYY | ON/OFF
1938 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1939 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1940 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1941 | Filter Sign |  | Reserved | Reserved
1942 | Swing
1943 | Room Temperature x10 °C | RO
1944 | HVAC Malfunction Code | RO
1945 | Lock Bits
1946 | Set Temperature Limits
1947 | Reserved
1948
1949
1950
1951
1952
VA number | 122 | Base Address = |  | 1953
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1953 | Operation Mode |  | UID Ln.XYY | ON/OFF
1954 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1955 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1956 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1957 | Filter Sign |  | Reserved | Reserved
1958 | Swing
1959 | Room Temperature x10 °C | RO
1960 | HVAC Malfunction Code | RO
1961 | Lock Bits
1962 | Set Temperature Limits
1963 | Reserved
1964
1965
1966
1967
1968
VA number | 123 | Base Address = |  | 1969
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1969 | Operation Mode |  | UID Ln.XYY | ON/OFF
1970 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1971 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1972 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1973 | Filter Sign |  | Reserved | Reserved
1974 | Swing
1975 | Room Temperature x10 °C | RO
1976 | HVAC Malfunction Code | RO
1977 | Lock Bits
1978 | Set Temperature Limits
1979 | Reserved
1980
1981
1982
1983
1984
VA number | 124 | Base Address = |  | 1985
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
1985 | Operation Mode |  | UID Ln.XYY | ON/OFF
1986 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
1987 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
1988 | ON/OFF |  | HVAC Malfunction CD | Inhibit
1989 | Filter Sign |  | Reserved | Reserved
1990 | Swing
1991 | Room Temperature x10 °C | RO
1992 | HVAC Malfunction Code | RO
1993 | Lock Bits
1994 | Set Temperature Limits
1995 | Reserved
1996
1997
1998
1999
2000
VA number | 125 | Base Address = |  | 2001
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
2001 | Operation Mode |  | UID Ln.XYY | ON/OFF
2002 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
2003 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
2004 | ON/OFF |  | HVAC Malfunction CD | Inhibit
2005 | Filter Sign |  | Reserved | Reserved
2006 | Swing
2007 | Room Temperature x10 °C | RO
2008 | HVAC Malfunction Code | RO
2009 | Lock Bits
2010 | Set Temperature Limits
2011 | Reserved
2012
2013
2014
2015
2016
VA number | 126 | Base Address = |  | 2017
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
2017 | Operation Mode |  | UID Ln.XYY | ON/OFF
2018 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
2019 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
2020 | ON/OFF |  | HVAC Malfunction CD | Inhibit
2021 | Filter Sign |  | Reserved | Reserved
2022 | Swing
2023 | Room Temperature x10 °C | RO
2024 | HVAC Malfunction Code | RO
2025 | Lock Bits
2026 | Set Temperature Limits
2027 | Reserved
2028
2029
2030
2031
2032
VA number | 127 | Base Address = |  | 2033
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
2033 | Operation Mode |  | UID Ln.XYY | ON/OFF
2034 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
2035 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
2036 | ON/OFF |  | HVAC Malfunction CD | Inhibit
2037 | Filter Sign |  | Reserved | Reserved
2038 | Swing
2039 | Room Temperature x10 °C | RO
2040 | HVAC Malfunction Code | RO
2041 | Lock Bits
2042 | Set Temperature Limits
2043 | Reserved
2044
2045
2046
2047
2048
VA number | 128 | Base Address = |  | 2049
Modbus Decimal Address | Function | R/W | Function | Function
| Holding Registers |  | Input Registers | Coils
2049 | Operation Mode |  | UID Ln.XYY | ON/OFF
2050 | Fan Speed |  | Room Temperature x10 °C | Filter Sign
2051 | Set Temperature x10 °C |  | HVAC Malfunction AB | Ext Terminals
2052 | ON/OFF |  | HVAC Malfunction CD | Inhibit
2053 | Filter Sign |  | Reserved | Reserved
2054 | Swing
2055 | Room Temperature x10 °C | RO
2056 | HVAC Malfunction Code | RO
2057 | Lock Bits
2058 | Set Temperature Limits
2059 | Reserved
2060
2061
2062
2063
2064